## Regulatory_KPIs
scenario | Rated_Power_MW | EU_Size_Category | TWH_mean_C | TWH_min_C | TWH_max_C | ERF_annual_mean | Q_available_mean_kW | Q_negotiated_mean_kW
Edge_LC | 0.5 | Very small (<=500 kW) | 47.6 | 44.77 | 50 | 0.81 | 380.1 | 342
Mid_LC | 3.2 | Large (2-10 MW) | 47.6 | 44.77 | 50 | 0.81 | 2483.6 | 2235.2
Hyperscale_LC | 25 | Very large (>10 MW) | 46 | 43.64 | 48 | 0.81 | 19602.8 | 17642.6

## EED_Compliance
scenario | IT_power_kW | total_rated_kW | EU_size_category | Art12_applicable | Art26_applicable | WHR_active | ERF_mean | Art26_exception_required | TEE_estimated_eur_year | note
Edge_LC | 500 | 590 | Very small (<=500 kW) | TRUE | FALSE | TRUE | 0.81 | FALSE | 55000 | Reporting required (IT >= 500 kW); Below threshold (total 590 kW <= 1,000 kW)
Mid_LC | 3200 | 3765 | Large (2-10 MW) | TRUE | TRUE | TRUE | 0.81 | FALSE | 360000 | Reporting required (IT >= 500 kW); WHR obligation applies (total 3,765 kW > 1,000 kW)
Hyperscale_LC | 25000 | 29412 | Very large (>10 MW) | TRUE | TRUE | TRUE | 0.81 | FALSE | 2842000 | Reporting required (IT >= 500 kW); WHR obligation applies (total 29,412 kW > 1,000 kW)

## ERF_Sensitivity
scenario | cooling_technology | capture_fraction | ERF | Q_negotiated_mean_kW | TEE_baseline_eur_year | TEE_delta_eur_year | vs_baseline_pct
Edge_LC | air_cooled_rear_door | 0.7 | 0.49 | 266 | 55000 | -21728 | -39.51
Edge_LC | direct_liquid_cooling | 0.8 | 0.64 | 304 | 55000 | -11543 | -20.99
Edge_LC | single_phase_immersion_conservative | 0.9 | 0.81 | 342 | 55000 | 0 | 0
Edge_LC | single_phase_immersion_optimal | 0.95 | 0.9025 | 361.1 | 55000 | 6281 | 11.42
Edge_LC | full_immersion | 0.99 | 0.9801 | 376.3 | 55000 | 11550 | 21
Mid_LC | air_cooled_rear_door | 0.7 | 0.49 | 1738.5 | 360000 | -142222 | -39.51
Mid_LC | direct_liquid_cooling | 0.8 | 0.64 | 1986.8 | 360000 | -75556 | -20.99
Mid_LC | single_phase_immersion_conservative | 0.9 | 0.81 | 2235.2 | 360000 | 0 | 0
Mid_LC | single_phase_immersion_optimal | 0.95 | 0.9025 | 2359.4 | 360000 | 41111 | 11.42
Mid_LC | full_immersion | 0.99 | 0.9801 | 2458.7 | 360000 | 75600 | 21
Hyperscale_LC | air_cooled_rear_door | 0.7 | 0.49 | 13722 | 2842000 | -1122765 | -39.51
Hyperscale_LC | direct_liquid_cooling | 0.8 | 0.64 | 15682.3 | 2842000 | -596469 | -20.99
Hyperscale_LC | single_phase_immersion_conservative | 0.9 | 0.81 | 17642.6 | 2842000 | 0 | 0
Hyperscale_LC | single_phase_immersion_optimal | 0.95 | 0.9025 | 18622.7 | 2842000 | 324549 | 11.42
Hyperscale_LC | full_immersion | 0.99 | 0.9801 | 19406.8 | 2842000 | 596820 | 21

## Benchmark_Comparison
case_name | source | year | T_supply_C | Q_kW | ERF_published | closest_scenario | model_TWH_mean_C | model_ERF | T_delta_C | ERF_delta | plausibility_flag | upgrade_needed_model | notes
Bahnhof Pionen (Stockholm) | IEA HPT Annex 47 | 2023 | 68 | 600 |  | Edge_LC | 47.6 | 0.81 | 20.4 |  | outside_range | Heat pump required (ΔT=20.4°C) | Two series HPs; 67m pipe to DH return; 975 kW heat output
Aquasar ETH Zurich | ICEF SDC Roadmap 2025 | 2022 | 65 | 10 | 0.8 | Edge_LC | 47.6 | 0.81 | 17.4 | -0.01 | within_range | Heat pump required (ΔT=17.4°C) | Campus heating; ~80pct capture; $1.25M/year savings (includes cooling cost offset)
iDataCool Germany | ICEF SDC Roadmap 2025 | 2022 | 65 |  |  | Edge_LC | 47.6 | 0.81 | 17.4 |  | within_range | Heat pump required (ΔT=17.4°C) | HPC + adsorption chiller; hot-water cooling ~65 C
Meta Odense Denmark | ICEF SDC Roadmap 2025 | 2020 | 57.5 |  |  | Edge_LC | 47.6 | 0.81 | 9.9 |  | within_range | Heat pump required (ΔT=9.9°C) | HP to Fjernvarme Fyn; 7000+ homes served; operating since 2020
EcoDataCenter Falun | EcoDataCenter press release 2022 | 2022 | 55 |  |  | Edge_LC | 47.6 | 0.81 | 7.4 |  | within_range | Heat pump required (ΔT=7.4°C) | Climate-positive DC; WHR to DH + biofuel; Falun SE; 80 MW secured power