## Epsilon_Gate_LC
dc_name | process_name | t_dc_mean_c | t_dc_max_c | t_req_c | delta_t_vs_mean_c | delta_t_vs_max_c | upgrade_tech_mean | upgrade_tech_max | k | r | epsilon | pass_gate | note
Edge_LC | LowT_60C | 47.6 | 50 | 60 | 12.4 | 10 | HP | HP | 0.92 | 0.06 | 0.8648 | TRUE | HP; ΔT(mean)=12.4°C
Edge_LC | MidT_90C | 47.6 | 50 | 90 | 42.4 | 40 | HP | HP | 0.92 | 0.06 | 0.8648 | TRUE | HP; ΔT(mean)=42.4°C
Edge_LC | HighT_130C | 47.6 | 50 | 130 | 82.4 | 80 | CO2_HTHP | CO2_HTHP | 0.85 | 0.08 | 0.782 | TRUE | CO2_HTHP; ΔT(mean)=82.4°C
Mid_LC | LowT_60C | 47.6 | 50 | 60 | 12.4 | 10 | HP | HP | 0.92 | 0.06 | 0.8648 | TRUE | HP; ΔT(mean)=12.4°C
Mid_LC | MidT_90C | 47.6 | 50 | 90 | 42.4 | 40 | HP | HP | 0.92 | 0.06 | 0.8648 | TRUE | HP; ΔT(mean)=42.4°C
Mid_LC | HighT_130C | 47.6 | 50 | 130 | 82.4 | 80 | CO2_HTHP | CO2_HTHP | 0.85 | 0.08 | 0.782 | TRUE | CO2_HTHP; ΔT(mean)=82.4°C
Hyperscale_LC | LowT_60C | 46 | 48 | 60 | 14 | 12 | HP | HP | 0.92 | 0.06 | 0.8648 | TRUE | HP; ΔT(mean)=14.0°C
Hyperscale_LC | MidT_90C | 46 | 48 | 90 | 44 | 42 | HP | HP | 0.92 | 0.06 | 0.8648 | TRUE | HP; ΔT(mean)=44.0°C
Hyperscale_LC | HighT_130C | 46 | 48 | 130 | 84 | 82 | CO2_HTHP | CO2_HTHP | 0.85 | 0.08 | 0.782 | TRUE | CO2_HTHP; ΔT(mean)=84.0°C

## Dataset_CE-HEAT_LC
dc_name | dc_q_nominal_kw | dc_t_supply_mean_c | dc_t_supply_max_c | dc_t_avail_fraction | plant_name | plant_description | plant_tier | plant_proximity_band | plant_t_req_c | plant_q_demand_kw | plant_shift_pattern | plant_delta_tc_baseline | plant_data_source | distance_km | RI_quantity | RI_temperature | RI_availability | RI_distance | RI_static | feasible
Edge_LC | 475 | 47.6 | 50 | 1 | LowT_01_Food_Short | Food drying - short proximity scenario [parametric, ENEA] | LowT_60C | short | 60 | 800 | 2shift | 0.25 | Parametric - ENEA IS benchmark (2021) | 30 | 0.5938 | 0.7334 | 0.65 | 0.85 | 0.5837 | 1
Edge_LC | 475 | 47.6 | 50 | 1 | LowT_02_Agro_Medium | Agro-industrial processing - medium proximity scenario [parametric, ENEA] | LowT_60C | medium | 60 | 1200 | 2shift | 0.28 | Parametric - ENEA IS benchmark (2021) | 75 | 0.3958 | 0.7334 | 0.65 | 0.625 | 0.4919 | 0
Edge_LC | 475 | 47.6 | 50 | 1 | LowT_03_Dairy_Short | Dairy processing - short proximity scenario [parametric, ENEA] | LowT_60C | short | 65 | 650 | continuous | 0.22 | Parametric - ENEA IS benchmark (2021) | 45 | 0.7308 | 0.6473 | 0.95 | 0.775 | 0.6347 | 1
Edge_LC | 475 | 47.6 | 50 | 1 | MidT_04_PaperPulp_Medium | Paper/pulp mill - medium proximity [parametric, Hotmaps-informed] | MidT_90C | medium | 90 | 28127.9 | continuous | 0.42 | Parametric - Hotmaps EU Paper statistics [Manz & Fleiter 2018, DOI:10.5281/zenodo.4687147]; T-profile: Fleiter et al. (2013) | 80 | 0.0169 | 0.3465 | 0.95 | 0.6 | 0.247 | 0
Edge_LC | 475 | 47.6 | 50 | 1 | MidT_05_PaperPulp_Short | Paper/pulp mill - short proximity [parametric, Hotmaps-informed] | MidT_90C | short | 90 | 31141.6 | continuous | 0.4 | Parametric - Hotmaps EU Paper statistics [Manz & Fleiter 2018, DOI:10.5281/zenodo.4687147]; T-profile: Fleiter et al. (2013) | 50 | 0.0153 | 0.3465 | 0.95 | 0.75 | 0.2614 | 0
Edge_LC | 475 | 47.6 | 50 | 1 | MidT_06_PaperPulp_Long | Paper/pulp mill - long proximity [parametric, Hotmaps-informed] | MidT_90C | long | 90 | 21095.9 | continuous | 0.45 | Parametric - Hotmaps EU Paper statistics [Manz & Fleiter 2018, DOI:10.5281/zenodo.4687147]; T-profile: Fleiter et al. (2013) | 140 | 0.0225 | 0.3465 | 0.95 | 0.3 | 0.219 | 0
Edge_LC | 475 | 47.6 | 50 | 1 | HighT_07_Rubber_Medium | Rubber vulcanisation - medium proximity [parametric, CE-HEAT] | HighT_130C | medium | 130 | 2800 | 2shift | 0.55 | Parametric - CE-HEAT taxonomy (WP3/WP4) | 100 | 0.1696 | 0.1275 | 0.65 | 0.5 | 0.1579 | 0
Edge_LC | 475 | 47.6 | 50 | 1 | HighT_08_ChemProcess_Short | Chemical process - short proximity [parametric, CE-HEAT] | HighT_130C | medium | 130 | 4500 | continuous | 0.58 | Parametric - CE-HEAT taxonomy (WP3/WP4) | 55 | 0.1056 | 0.1275 | 0.95 | 0.725 | 0.2029 | 0
Edge_LC | 475 | 47.6 | 50 | 1 | HighT_09_Steam_Long | Industrial steam - long proximity [parametric, CE-HEAT] | HighT_130C | long | 135 | 6200 | continuous | 0.6 | Parametric - CE-HEAT taxonomy (WP3/WP4) | 160 | 0.0766 | 0.1125 | 0.95 | 0.2 | 0.1343 | 0
Mid_LC | 3104 | 47.6 | 50 | 1 | LowT_01_Food_Short | Food drying - short proximity scenario [parametric, ENEA] | LowT_60C | short | 60 | 800 | 2shift | 0.25 | Parametric - ENEA IS benchmark (2021) | 30 | 1 | 0.7334 | 0.65 | 0.85 | 0.7259 | 1
Mid_LC | 3104 | 47.6 | 50 | 1 | LowT_02_Agro_Medium | Agro-industrial processing - medium proximity scenario [parametric, ENEA] | LowT_60C | medium | 60 | 1200 | 2shift | 0.28 | Parametric - ENEA IS benchmark (2021) | 75 | 1 | 0.7334 | 0.65 | 0.625 | 0.7034 | 1
Mid_LC | 3104 | 47.6 | 50 | 1 | LowT_03_Dairy_Short | Dairy processing - short proximity scenario [parametric, ENEA] | LowT_60C | short | 65 | 650 | continuous | 0.22 | Parametric - ENEA IS benchmark (2021) | 45 | 1 | 0.6473 | 0.95 | 0.775 | 0.7289 | 1
Mid_LC | 3104 | 47.6 | 50 | 1 | MidT_04_PaperPulp_Medium | Paper/pulp mill - medium proximity [parametric, Hotmaps-informed] | MidT_90C | medium | 90 | 28127.9 | continuous | 0.42 | Parametric - Hotmaps EU Paper statistics [Manz & Fleiter 2018, DOI:10.5281/zenodo.4687147]; T-profile: Fleiter et al. (2013) | 80 | 0.1104 | 0.3465 | 0.95 | 0.6 | 0.2797 | 0
Mid_LC | 3104 | 47.6 | 50 | 1 | MidT_05_PaperPulp_Short | Paper/pulp mill - short proximity [parametric, Hotmaps-informed] | MidT_90C | short | 90 | 31141.6 | continuous | 0.4 | Parametric - Hotmaps EU Paper statistics [Manz & Fleiter 2018, DOI:10.5281/zenodo.4687147]; T-profile: Fleiter et al. (2013) | 50 | 0.0997 | 0.3465 | 0.95 | 0.75 | 0.291 | 0
Mid_LC | 3104 | 47.6 | 50 | 1 | MidT_06_PaperPulp_Long | Paper/pulp mill - long proximity [parametric, Hotmaps-informed] | MidT_90C | long | 90 | 21095.9 | continuous | 0.45 | Parametric - Hotmaps EU Paper statistics [Manz & Fleiter 2018, DOI:10.5281/zenodo.4687147]; T-profile: Fleiter et al. (2013) | 140 | 0.1471 | 0.3465 | 0.95 | 0.3 | 0.2626 | 0
Mid_LC | 3104 | 47.6 | 50 | 1 | HighT_07_Rubber_Medium | Rubber vulcanisation - medium proximity [parametric, CE-HEAT] | HighT_130C | medium | 130 | 2800 | 2shift | 0.55 | Parametric - CE-HEAT taxonomy (WP3/WP4) | 100 | 1 | 0.1275 | 0.65 | 0.5 | 0.4485 | 0
Mid_LC | 3104 | 47.6 | 50 | 1 | HighT_08_ChemProcess_Short | Chemical process - short proximity [parametric, CE-HEAT] | HighT_130C | medium | 130 | 4500 | continuous | 0.58 | Parametric - CE-HEAT taxonomy (WP3/WP4) | 55 | 0.6898 | 0.1275 | 0.95 | 0.725 | 0.4074 | 0
Mid_LC | 3104 | 47.6 | 50 | 1 | HighT_09_Steam_Long | Industrial steam - long proximity [parametric, CE-HEAT] | HighT_130C | long | 135 | 6200 | continuous | 0.6 | Parametric - CE-HEAT taxonomy (WP3/WP4) | 160 | 0.5006 | 0.1125 | 0.95 | 0.2 | 0.2827 | 0
Hyperscale_LC | 24500 | 46 | 49.5 | 1 | LowT_01_Food_Short | Food drying - short proximity scenario [parametric, ENEA] | LowT_60C | short | 60 | 800 | 2shift | 0.25 | Parametric - ENEA IS benchmark (2021) | 30 | 1 | 0.7047 | 0.65 | 0.85 | 0.7144 | 1
Hyperscale_LC | 24500 | 46 | 49.5 | 1 | LowT_02_Agro_Medium | Agro-industrial processing - medium proximity scenario [parametric, ENEA] | LowT_60C | medium | 60 | 1200 | 2shift | 0.28 | Parametric - ENEA IS benchmark (2021) | 75 | 1 | 0.7047 | 0.65 | 0.625 | 0.6919 | 1
Hyperscale_LC | 24500 | 46 | 49.5 | 1 | LowT_03_Dairy_Short | Dairy processing - short proximity scenario [parametric, ENEA] | LowT_60C | short | 65 | 650 | continuous | 0.22 | Parametric - ENEA IS benchmark (2021) | 45 | 1 | 0.6219 | 0.95 | 0.775 | 0.7188 | 1
Hyperscale_LC | 24500 | 46 | 49.5 | 1 | MidT_04_PaperPulp_Medium | Paper/pulp mill - medium proximity [parametric, Hotmaps-informed] | MidT_90C | medium | 90 | 28127.9 | continuous | 0.42 | Parametric - Hotmaps EU Paper statistics [Manz & Fleiter 2018, DOI:10.5281/zenodo.4687147]; T-profile: Fleiter et al. (2013) | 80 | 0.871 | 0.3329 | 0.95 | 0.6 | 0.5405 | 1
Hyperscale_LC | 24500 | 46 | 49.5 | 1 | MidT_05_PaperPulp_Short | Paper/pulp mill - short proximity [parametric, Hotmaps-informed] | MidT_90C | short | 90 | 31141.6 | continuous | 0.4 | Parametric - Hotmaps EU Paper statistics [Manz & Fleiter 2018, DOI:10.5281/zenodo.4687147]; T-profile: Fleiter et al. (2013) | 50 | 0.7867 | 0.3329 | 0.95 | 0.75 | 0.526 | 1
Hyperscale_LC | 24500 | 46 | 49.5 | 1 | MidT_06_PaperPulp_Long | Paper/pulp mill - long proximity [parametric, Hotmaps-informed] | MidT_90C | long | 90 | 21095.9 | continuous | 0.45 | Parametric - Hotmaps EU Paper statistics [Manz & Fleiter 2018, DOI:10.5281/zenodo.4687147]; T-profile: Fleiter et al. (2013) | 140 | 1 | 0.3329 | 0.95 | 0.3 | 0.5556 | 1
Hyperscale_LC | 24500 | 46 | 49.5 | 1 | HighT_07_Rubber_Medium | Rubber vulcanisation - medium proximity [parametric, CE-HEAT] | HighT_130C | medium | 130 | 2800 | 2shift | 0.55 | Parametric - CE-HEAT taxonomy (WP3/WP4) | 100 | 1 | 0.1225 | 0.65 | 0.5 | 0.4465 | 0
Hyperscale_LC | 24500 | 46 | 49.5 | 1 | HighT_08_ChemProcess_Short | Chemical process - short proximity [parametric, CE-HEAT] | HighT_130C | medium | 130 | 4500 | continuous | 0.58 | Parametric - CE-HEAT taxonomy (WP3/WP4) | 55 | 1 | 0.1225 | 0.95 | 0.725 | 0.514 | 1
Hyperscale_LC | 24500 | 46 | 49.5 | 1 | HighT_09_Steam_Long | Industrial steam - long proximity [parametric, CE-HEAT] | HighT_130C | long | 135 | 6200 | continuous | 0.6 | Parametric - CE-HEAT taxonomy (WP3/WP4) | 160 | 1 | 0.1081 | 0.95 | 0.2 | 0.4557 | 0

## Dataset_Summary_LC
dc_name | tier | data_source | n_pairs | n_feasible | RI_static_mean | RI_static_max | RI_temp_mean | dist_mean_km
Edge_LC | LowT_60C | Parametric (ENEA 2021) | 3 | 2 | 0.5701 | 0.6347 | 0.7047 | 50
Mid_LC | LowT_60C | Parametric (ENEA 2021) | 3 | 3 | 0.7194 | 0.7289 | 0.7047 | 50
Hyperscale_LC | LowT_60C | Parametric (ENEA 2021) | 3 | 3 | 0.7084 | 0.7188 | 0.6771 | 50
Edge_LC | MidT_90C | Parametric - Hotmaps-informed (Manz & Fleiter 2018) | 3 | 0 | 0.2425 | 0.2614 | 0.3465 | 90
Mid_LC | MidT_90C | Parametric - Hotmaps-informed (Manz & Fleiter 2018) | 3 | 0 | 0.2778 | 0.291 | 0.3465 | 90
Hyperscale_LC | MidT_90C | Parametric - Hotmaps-informed (Manz & Fleiter 2018) | 3 | 3 | 0.5407 | 0.5556 | 0.3329 | 90
Edge_LC | HighT_130C | Parametric (CE-HEAT WP3/WP4) | 3 | 0 | 0.165 | 0.2029 | 0.1225 | 105
Mid_LC | HighT_130C | Parametric (CE-HEAT WP3/WP4) | 3 | 0 | 0.3795 | 0.4485 | 0.1225 | 105
Hyperscale_LC | HighT_130C | Parametric (CE-HEAT WP3/WP4) | 3 | 1 | 0.4721 | 0.514 | 0.1177 | 105

## IS_Match_Scores_LC
rank | dc_name | process_name | ri_temporal | exergy_dt_norm | delta_tc_norm | is_match_score | is_match_score_raw | tier | beta | gamma | delta | n_weighted_steps | exergy_norm_method
1 | Edge_LC | LowT_60C | 0.7419 | 0.7529 | 0.25 | 0.5479 | 0.5479 | marginal | 0.4 | 0.4 | 0.2 | 16704 | per_scenario
2 | Mid_LC | LowT_60C | 0.7419 | 0.7529 | 0.25 | 0.5479 | 0.5479 | marginal | 0.4 | 0.4 | 0.2 | 16704 | per_scenario
3 | Hyperscale_LC | LowT_60C | 0.7358 | 0.7583 | 0.25 | 0.5476 | 0.5476 | marginal | 0.4 | 0.4 | 0.2 | 16704 | per_scenario
4 | Mid_LC | MidT_90C | 0.5916 | 0.7529 | 0.4233 | 0.4532 | 0.4532 | marginal | 0.4 | 0.4 | 0.2 | 35040 | per_scenario
5 | Edge_LC | MidT_90C | 0.5916 | 0.7529 | 0.4233 | 0.4532 | 0.4532 | marginal | 0.4 | 0.4 | 0.2 | 35040 | per_scenario
6 | Hyperscale_LC | MidT_90C | 0.586 | 0.7583 | 0.4233 | 0.4531 | 0.4531 | marginal | 0.4 | 0.4 | 0.2 | 35040 | per_scenario
7 | Edge_LC | HighT_130C | 0.4556 | 0.7529 | 0.5767 | 0.3681 | 0.3681 | marginal | 0.4 | 0.4 | 0.2 | 16704 | per_scenario
8 | Mid_LC | HighT_130C | 0.4556 | 0.7529 | 0.5767 | 0.3681 | 0.3681 | marginal | 0.4 | 0.4 | 0.2 | 16704 | per_scenario
9 | Hyperscale_LC | HighT_130C | 0.4496 | 0.7583 | 0.5767 | 0.3678 | 0.3678 | marginal | 0.4 | 0.4 | 0.2 | 16704 | per_scenario

## IS_Match_Sensitivity_LC
beta | gamma | delta | dc_name | process_name | is_match_score | tier
0.2 | 0.2 | 0.6 | Edge_LC | HighT_130C | 0 | not_viable
0.2 | 0.2 | 0.6 | Edge_LC | LowT_60C | 0.149 | not_viable
0.2 | 0.2 | 0.6 | Edge_LC | MidT_90C | 0.0149 | not_viable
0.2 | 0.2 | 0.6 | Mid_LC | HighT_130C | 0 | not_viable
0.2 | 0.2 | 0.6 | Mid_LC | LowT_60C | 0.149 | not_viable
0.2 | 0.2 | 0.6 | Mid_LC | MidT_90C | 0.0149 | not_viable
0.2 | 0.2 | 0.6 | Hyperscale_LC | HighT_130C | 0 | not_viable
0.2 | 0.2 | 0.6 | Hyperscale_LC | LowT_60C | 0.1488 | not_viable
0.2 | 0.2 | 0.6 | Hyperscale_LC | MidT_90C | 0.0149 | not_viable
0.2 | 0.3 | 0.5 | Edge_LC | HighT_130C | 0.0287 | not_viable
0.2 | 0.3 | 0.5 | Edge_LC | LowT_60C | 0.2493 | not_viable
0.2 | 0.3 | 0.5 | Edge_LC | MidT_90C | 0.1325 | not_viable
0.2 | 0.3 | 0.5 | Mid_LC | HighT_130C | 0.0287 | not_viable
0.2 | 0.3 | 0.5 | Mid_LC | LowT_60C | 0.2493 | not_viable
0.2 | 0.3 | 0.5 | Mid_LC | MidT_90C | 0.1325 | not_viable
0.2 | 0.3 | 0.5 | Hyperscale_LC | HighT_130C | 0.0291 | not_viable
0.2 | 0.3 | 0.5 | Hyperscale_LC | LowT_60C | 0.2497 | not_viable
0.2 | 0.3 | 0.5 | Hyperscale_LC | MidT_90C | 0.133 | not_viable
0.2 | 0.4 | 0.4 | Edge_LC | HighT_130C | 0.1616 | not_viable
0.2 | 0.4 | 0.4 | Edge_LC | LowT_60C | 0.3496 | marginal
0.2 | 0.4 | 0.4 | Edge_LC | MidT_90C | 0.2502 | not_viable
0.2 | 0.4 | 0.4 | Mid_LC | HighT_130C | 0.1616 | not_viable
0.2 | 0.4 | 0.4 | Mid_LC | LowT_60C | 0.3496 | marginal
0.2 | 0.4 | 0.4 | Mid_LC | MidT_90C | 0.2502 | not_viable
0.2 | 0.4 | 0.4 | Hyperscale_LC | HighT_130C | 0.1626 | not_viable
0.2 | 0.4 | 0.4 | Hyperscale_LC | LowT_60C | 0.3505 | marginal
0.2 | 0.4 | 0.4 | Hyperscale_LC | MidT_90C | 0.2512 | not_viable
0.2 | 0.5 | 0.3 | Edge_LC | HighT_130C | 0.2946 | not_viable
0.2 | 0.5 | 0.3 | Edge_LC | LowT_60C | 0.4498 | marginal
0.2 | 0.5 | 0.3 | Edge_LC | MidT_90C | 0.3678 | marginal
0.2 | 0.5 | 0.3 | Mid_LC | HighT_130C | 0.2946 | not_viable
0.2 | 0.5 | 0.3 | Mid_LC | LowT_60C | 0.4498 | marginal
0.2 | 0.5 | 0.3 | Mid_LC | MidT_90C | 0.3678 | marginal
0.2 | 0.5 | 0.3 | Hyperscale_LC | HighT_130C | 0.2961 | not_viable
0.2 | 0.5 | 0.3 | Hyperscale_LC | LowT_60C | 0.4513 | marginal
0.2 | 0.5 | 0.3 | Hyperscale_LC | MidT_90C | 0.3694 | marginal
0.3 | 0.2 | 0.5 | Edge_LC | HighT_130C | 0 | not_viable
0.3 | 0.2 | 0.5 | Edge_LC | LowT_60C | 0.2482 | not_viable
0.3 | 0.2 | 0.5 | Edge_LC | MidT_90C | 0.1164 | not_viable
0.3 | 0.2 | 0.5 | Mid_LC | HighT_130C | 0 | not_viable
0.3 | 0.2 | 0.5 | Mid_LC | LowT_60C | 0.2482 | not_viable
0.3 | 0.2 | 0.5 | Mid_LC | MidT_90C | 0.1164 | not_viable
0.3 | 0.2 | 0.5 | Hyperscale_LC | HighT_130C | 0 | not_viable
0.3 | 0.2 | 0.5 | Hyperscale_LC | LowT_60C | 0.2474 | not_viable
0.3 | 0.2 | 0.5 | Hyperscale_LC | MidT_90C | 0.1158 | not_viable
0.3 | 0.3 | 0.4 | Edge_LC | HighT_130C | 0.1319 | not_viable
0.3 | 0.3 | 0.4 | Edge_LC | LowT_60C | 0.3484 | marginal
0.3 | 0.3 | 0.4 | Edge_LC | MidT_90C | 0.234 | not_viable
0.3 | 0.3 | 0.4 | Mid_LC | HighT_130C | 0.1319 | not_viable
0.3 | 0.3 | 0.4 | Mid_LC | LowT_60C | 0.3484 | marginal
0.3 | 0.3 | 0.4 | Mid_LC | MidT_90C | 0.234 | not_viable
0.3 | 0.3 | 0.4 | Hyperscale_LC | HighT_130C | 0.1317 | not_viable
0.3 | 0.3 | 0.4 | Hyperscale_LC | LowT_60C | 0.3482 | marginal
0.3 | 0.3 | 0.4 | Hyperscale_LC | MidT_90C | 0.234 | not_viable
0.3 | 0.4 | 0.3 | Edge_LC | HighT_130C | 0.2649 | not_viable
0.3 | 0.4 | 0.3 | Edge_LC | LowT_60C | 0.4487 | marginal
0.3 | 0.4 | 0.3 | Edge_LC | MidT_90C | 0.3517 | marginal
0.3 | 0.4 | 0.3 | Mid_LC | HighT_130C | 0.2649 | not_viable
0.3 | 0.4 | 0.3 | Mid_LC | LowT_60C | 0.4487 | marginal
0.3 | 0.4 | 0.3 | Mid_LC | MidT_90C | 0.3517 | marginal
0.3 | 0.4 | 0.3 | Hyperscale_LC | HighT_130C | 0.2652 | not_viable
0.3 | 0.4 | 0.3 | Hyperscale_LC | LowT_60C | 0.4491 | marginal
0.3 | 0.4 | 0.3 | Hyperscale_LC | MidT_90C | 0.3521 | marginal
0.3 | 0.5 | 0.2 | Edge_LC | HighT_130C | 0.3978 | marginal
0.3 | 0.5 | 0.2 | Edge_LC | LowT_60C | 0.549 | marginal
0.3 | 0.5 | 0.2 | Edge_LC | MidT_90C | 0.4693 | marginal
0.3 | 0.5 | 0.2 | Mid_LC | HighT_130C | 0.3978 | marginal
0.3 | 0.5 | 0.2 | Mid_LC | LowT_60C | 0.549 | marginal
0.3 | 0.5 | 0.2 | Mid_LC | MidT_90C | 0.4693 | marginal
0.3 | 0.5 | 0.2 | Hyperscale_LC | HighT_130C | 0.3987 | marginal
0.3 | 0.5 | 0.2 | Hyperscale_LC | LowT_60C | 0.5499 | marginal
0.3 | 0.5 | 0.2 | Hyperscale_LC | MidT_90C | 0.4703 | marginal
0.4 | 0.2 | 0.4 | Edge_LC | HighT_130C | 0.1022 | not_viable
0.4 | 0.2 | 0.4 | Edge_LC | LowT_60C | 0.3473 | marginal
0.4 | 0.2 | 0.4 | Edge_LC | MidT_90C | 0.2179 | not_viable
0.4 | 0.2 | 0.4 | Mid_LC | HighT_130C | 0.1022 | not_viable
0.4 | 0.2 | 0.4 | Mid_LC | LowT_60C | 0.3473 | marginal
0.4 | 0.2 | 0.4 | Mid_LC | MidT_90C | 0.2179 | not_viable
0.4 | 0.2 | 0.4 | Hyperscale_LC | HighT_130C | 0.1008 | not_viable
0.4 | 0.2 | 0.4 | Hyperscale_LC | LowT_60C | 0.346 | marginal
0.4 | 0.2 | 0.4 | Hyperscale_LC | MidT_90C | 0.2167 | not_viable
0.4 | 0.3 | 0.3 | Edge_LC | HighT_130C | 0.2351 | not_viable
0.4 | 0.3 | 0.3 | Edge_LC | LowT_60C | 0.4476 | marginal
0.4 | 0.3 | 0.3 | Edge_LC | MidT_90C | 0.3355 | marginal
0.4 | 0.3 | 0.3 | Mid_LC | HighT_130C | 0.2351 | not_viable
0.4 | 0.3 | 0.3 | Mid_LC | LowT_60C | 0.4476 | marginal
0.4 | 0.3 | 0.3 | Mid_LC | MidT_90C | 0.3355 | marginal
0.4 | 0.3 | 0.3 | Hyperscale_LC | HighT_130C | 0.2343 | not_viable
0.4 | 0.3 | 0.3 | Hyperscale_LC | LowT_60C | 0.4468 | marginal
0.4 | 0.3 | 0.3 | Hyperscale_LC | MidT_90C | 0.3349 | marginal
0.4 | 0.4 | 0.2 | Edge_LC | HighT_130C | 0.3681 | marginal
0.4 | 0.4 | 0.2 | Edge_LC | LowT_60C | 0.5479 | marginal
0.4 | 0.4 | 0.2 | Edge_LC | MidT_90C | 0.4532 | marginal
0.4 | 0.4 | 0.2 | Mid_LC | HighT_130C | 0.3681 | marginal
0.4 | 0.4 | 0.2 | Mid_LC | LowT_60C | 0.5479 | marginal
0.4 | 0.4 | 0.2 | Mid_LC | MidT_90C | 0.4532 | marginal
0.4 | 0.4 | 0.2 | Hyperscale_LC | HighT_130C | 0.3678 | marginal
0.4 | 0.4 | 0.2 | Hyperscale_LC | LowT_60C | 0.5476 | marginal
0.4 | 0.4 | 0.2 | Hyperscale_LC | MidT_90C | 0.4531 | marginal
0.4 | 0.5 | 0.1 | Edge_LC | HighT_130C | 0.5011 | marginal
0.4 | 0.5 | 0.1 | Edge_LC | LowT_60C | 0.6482 | high_priority
0.4 | 0.5 | 0.1 | Edge_LC | MidT_90C | 0.5708 | marginal
0.4 | 0.5 | 0.1 | Mid_LC | HighT_130C | 0.5011 | marginal
0.4 | 0.5 | 0.1 | Mid_LC | LowT_60C | 0.6482 | high_priority
0.4 | 0.5 | 0.1 | Mid_LC | MidT_90C | 0.5708 | marginal
0.4 | 0.5 | 0.1 | Hyperscale_LC | HighT_130C | 0.5013 | marginal
0.4 | 0.5 | 0.1 | Hyperscale_LC | LowT_60C | 0.6485 | high_priority
0.4 | 0.5 | 0.1 | Hyperscale_LC | MidT_90C | 0.5712 | marginal
0.5 | 0.2 | 0.3 | Edge_LC | HighT_130C | 0.2054 | not_viable
0.5 | 0.2 | 0.3 | Edge_LC | LowT_60C | 0.4465 | marginal
0.5 | 0.2 | 0.3 | Edge_LC | MidT_90C | 0.3194 | marginal
0.5 | 0.2 | 0.3 | Mid_LC | HighT_130C | 0.2054 | not_viable
0.5 | 0.2 | 0.3 | Mid_LC | LowT_60C | 0.4465 | marginal
0.5 | 0.2 | 0.3 | Mid_LC | MidT_90C | 0.3194 | marginal
0.5 | 0.2 | 0.3 | Hyperscale_LC | HighT_130C | 0.2034 | not_viable
0.5 | 0.2 | 0.3 | Hyperscale_LC | LowT_60C | 0.4446 | marginal
0.5 | 0.2 | 0.3 | Hyperscale_LC | MidT_90C | 0.3177 | marginal
0.5 | 0.3 | 0.2 | Edge_LC | HighT_130C | 0.3384 | marginal
0.5 | 0.3 | 0.2 | Edge_LC | LowT_60C | 0.5468 | marginal
0.5 | 0.3 | 0.2 | Edge_LC | MidT_90C | 0.437 | marginal
0.5 | 0.3 | 0.2 | Mid_LC | HighT_130C | 0.3384 | marginal
0.5 | 0.3 | 0.2 | Mid_LC | LowT_60C | 0.5468 | marginal
0.5 | 0.3 | 0.2 | Mid_LC | MidT_90C | 0.437 | marginal
0.5 | 0.3 | 0.2 | Hyperscale_LC | HighT_130C | 0.3369 | marginal
0.5 | 0.3 | 0.2 | Hyperscale_LC | LowT_60C | 0.5454 | marginal
0.5 | 0.3 | 0.2 | Hyperscale_LC | MidT_90C | 0.4358 | marginal
0.5 | 0.4 | 0.1 | Edge_LC | HighT_130C | 0.4713 | marginal
0.5 | 0.4 | 0.1 | Edge_LC | LowT_60C | 0.6471 | high_priority
0.5 | 0.4 | 0.1 | Edge_LC | MidT_90C | 0.5547 | marginal
0.5 | 0.4 | 0.1 | Mid_LC | HighT_130C | 0.4713 | marginal
0.5 | 0.4 | 0.1 | Mid_LC | LowT_60C | 0.6471 | high_priority
0.5 | 0.4 | 0.1 | Mid_LC | MidT_90C | 0.5547 | marginal
0.5 | 0.4 | 0.1 | Hyperscale_LC | HighT_130C | 0.4704 | marginal
0.5 | 0.4 | 0.1 | Hyperscale_LC | LowT_60C | 0.6462 | high_priority
0.5 | 0.4 | 0.1 | Hyperscale_LC | MidT_90C | 0.554 | marginal
0.5 | 0.5 | 0 | Edge_LC | HighT_130C | 0.6043 | high_priority
0.5 | 0.5 | 0 | Edge_LC | LowT_60C | 0.7474 | high_priority
0.5 | 0.5 | 0 | Edge_LC | MidT_90C | 0.6723 | high_priority
0.5 | 0.5 | 0 | Mid_LC | HighT_130C | 0.6043 | high_priority
0.5 | 0.5 | 0 | Mid_LC | LowT_60C | 0.7474 | high_priority
0.5 | 0.5 | 0 | Mid_LC | MidT_90C | 0.6723 | high_priority
0.5 | 0.5 | 0 | Hyperscale_LC | HighT_130C | 0.6039 | high_priority
0.5 | 0.5 | 0 | Hyperscale_LC | LowT_60C | 0.7471 | high_priority
0.5 | 0.5 | 0 | Hyperscale_LC | MidT_90C | 0.6722 | high_priority

## Ranking_Metrics_LC
method | scope | ndcg_at_9 | precision_at_3 | n_marginal_plus | n_feasible_baseline | n_pairs
IS-Match_LC | Edge_LC | 0.9884 | 1 | 9 | 2 | 9
IS-Match_LC | Mid_LC | 0.9881 | 1 | 9 | 3 | 9
IS-Match_LC | Hyperscale_LC | 0.9985 | 1 | 9 | 7 | 9
IS-Match_LC | ALL_pooled | 0.9759 | 0.3333 | 27 | 12 | 27
RI_temporal_baseline | Edge_LC | 0.9778 | 1 | 9 | 2 | 9
RI_temporal_baseline | Mid_LC | 0.9863 | 1 | 9 | 3 | 9
RI_temporal_baseline | Hyperscale_LC | 0.9971 | 1 | 9 | 7 | 9
RI_temporal_baseline | ALL_pooled | 0.9711 | 0.3333 | 27 | 12 | 27

## Ranking_Sensitivity_LC
beta | gamma | delta | ndcg_mean | ndcg_min | ndcg_max
0.2 | 0.2 | 0.6 | 0.997 | 0.9917 | 1
0.2 | 0.3 | 0.5 | 0.9956 | 0.9886 | 0.9995
0.2 | 0.4 | 0.4 | 0.9956 | 0.9886 | 0.9995
0.3 | 0.2 | 0.5 | 0.9956 | 0.9886 | 0.9995
0.4 | 0.4 | 0.2 | 0.9917 | 0.9881 | 0.9985
0.4 | 0.5 | 0.1 | 0.9917 | 0.9878 | 0.9985
0.5 | 0.3 | 0.2 | 0.9917 | 0.9878 | 0.9985
0.2 | 0.5 | 0.3 | 0.9915 | 0.9881 | 0.998
0.3 | 0.3 | 0.4 | 0.9915 | 0.9881 | 0.998
0.3 | 0.4 | 0.3 | 0.9915 | 0.9881 | 0.998
0.3 | 0.5 | 0.2 | 0.9915 | 0.9881 | 0.998
0.4 | 0.2 | 0.4 | 0.9915 | 0.9881 | 0.998
0.4 | 0.3 | 0.3 | 0.9915 | 0.9881 | 0.998
0.5 | 0.2 | 0.3 | 0.9915 | 0.9881 | 0.998
0.5 | 0.4 | 0.1 | 0.9871 | 0.9778 | 0.9971
0.5 | 0.5 | 0 | 0.9871 | 0.9778 | 0.9971

## DeltaTC_Calibration_LC
rank | dc_name | process_name | ri_temporal | exergy_dt_norm | delta_tc_norm | is_match_score | is_match_score_raw | tier | beta | gamma | delta | n_weighted_steps | exergy_norm_method | iteration
1 | Edge_LC | LowT_60C | 0.7419 | 0.7529 | 0.25 | 0.5479 | 0.5479 | marginal | 0.4 | 0.4 | 0.2 | 16704 | per_scenario | 0
2 | Mid_LC | LowT_60C | 0.7419 | 0.7529 | 0.25 | 0.5479 | 0.5479 | marginal | 0.4 | 0.4 | 0.2 | 16704 | per_scenario | 0
3 | Hyperscale_LC | LowT_60C | 0.7358 | 0.7583 | 0.25 | 0.5476 | 0.5476 | marginal | 0.4 | 0.4 | 0.2 | 16704 | per_scenario | 0
4 | Mid_LC | MidT_90C | 0.5916 | 0.7529 | 0.4233 | 0.4532 | 0.4532 | marginal | 0.4 | 0.4 | 0.2 | 35040 | per_scenario | 0
5 | Edge_LC | MidT_90C | 0.5916 | 0.7529 | 0.4233 | 0.4532 | 0.4532 | marginal | 0.4 | 0.4 | 0.2 | 35040 | per_scenario | 0
6 | Hyperscale_LC | MidT_90C | 0.586 | 0.7583 | 0.4233 | 0.4531 | 0.4531 | marginal | 0.4 | 0.4 | 0.2 | 35040 | per_scenario | 0
7 | Edge_LC | HighT_130C | 0.4556 | 0.7529 | 0.5767 | 0.3681 | 0.3681 | marginal | 0.4 | 0.4 | 0.2 | 16704 | per_scenario | 0
8 | Mid_LC | HighT_130C | 0.4556 | 0.7529 | 0.5767 | 0.3681 | 0.3681 | marginal | 0.4 | 0.4 | 0.2 | 16704 | per_scenario | 0
9 | Hyperscale_LC | HighT_130C | 0.4496 | 0.7583 | 0.5767 | 0.3678 | 0.3678 | marginal | 0.4 | 0.4 | 0.2 | 16704 | per_scenario | 0
1 | Edge_LC | LowT_60C | 0.7419 | 0.7529 | 0.17105 | 0.5637 | 0.5479 | marginal | 0.4 | 0.4 | 0.2 | 16704 | per_scenario | 1
2 | Mid_LC | LowT_60C | 0.7419 | 0.7529 | 0.17105 | 0.5637 | 0.5479 | marginal | 0.4 | 0.4 | 0.2 | 16704 | per_scenario | 1
3 | Hyperscale_LC | LowT_60C | 0.7358 | 0.7583 | 0.17105 | 0.5634 | 0.5476 | marginal | 0.4 | 0.4 | 0.2 | 16704 | per_scenario | 1
4 | Mid_LC | MidT_90C | 0.5916 | 0.7529 | 0.30787 | 0.4762 | 0.4532 | marginal | 0.4 | 0.4 | 0.2 | 35040 | per_scenario | 1
5 | Edge_LC | MidT_90C | 0.5916 | 0.7529 | 0.30787 | 0.4762 | 0.4532 | marginal | 0.4 | 0.4 | 0.2 | 35040 | per_scenario | 1
6 | Hyperscale_LC | MidT_90C | 0.586 | 0.7583 | 0.30787 | 0.4761 | 0.4531 | marginal | 0.4 | 0.4 | 0.2 | 35040 | per_scenario | 1
7 | Edge_LC | HighT_130C | 0.4556 | 0.7529 | 0.43829 | 0.3957 | 0.3681 | marginal | 0.4 | 0.4 | 0.2 | 16704 | per_scenario | 1
8 | Mid_LC | HighT_130C | 0.4556 | 0.7529 | 0.43829 | 0.3957 | 0.3681 | marginal | 0.4 | 0.4 | 0.2 | 16704 | per_scenario | 1
9 | Hyperscale_LC | HighT_130C | 0.4496 | 0.7583 | 0.43829 | 0.3955 | 0.3678 | marginal | 0.4 | 0.4 | 0.2 | 16704 | per_scenario | 1
1 | Edge_LC | LowT_60C | 0.7419 | 0.7529 | 0.11703 | 0.5745 | 0.5479 | marginal | 0.4 | 0.4 | 0.2 | 16704 | per_scenario | 2
2 | Mid_LC | LowT_60C | 0.7419 | 0.7529 | 0.11703 | 0.5745 | 0.5479 | marginal | 0.4 | 0.4 | 0.2 | 16704 | per_scenario | 2
3 | Hyperscale_LC | LowT_60C | 0.7358 | 0.7583 | 0.11703 | 0.5742 | 0.5476 | marginal | 0.4 | 0.4 | 0.2 | 16704 | per_scenario | 2
4 | Mid_LC | MidT_90C | 0.5916 | 0.7529 | 0.22391 | 0.493 | 0.4532 | marginal | 0.4 | 0.4 | 0.2 | 35040 | per_scenario | 2
5 | Edge_LC | MidT_90C | 0.5916 | 0.7529 | 0.22391 | 0.493 | 0.4532 | marginal | 0.4 | 0.4 | 0.2 | 35040 | per_scenario | 2
6 | Hyperscale_LC | MidT_90C | 0.586 | 0.7583 | 0.22391 | 0.4929 | 0.4531 | marginal | 0.4 | 0.4 | 0.2 | 35040 | per_scenario | 2
7 | Edge_LC | HighT_130C | 0.4556 | 0.7529 | 0.3331 | 0.4168 | 0.3681 | marginal | 0.4 | 0.4 | 0.2 | 16704 | per_scenario | 2
8 | Mid_LC | HighT_130C | 0.4556 | 0.7529 | 0.3331 | 0.4168 | 0.3681 | marginal | 0.4 | 0.4 | 0.2 | 16704 | per_scenario | 2
9 | Hyperscale_LC | HighT_130C | 0.4496 | 0.7583 | 0.3331 | 0.4165 | 0.3678 | marginal | 0.4 | 0.4 | 0.2 | 16704 | per_scenario | 2
1 | Edge_LC | LowT_60C | 0.7419 | 0.7529 | 0.08007 | 0.5819 | 0.5479 | marginal | 0.4 | 0.4 | 0.2 | 16704 | per_scenario | 3
2 | Mid_LC | LowT_60C | 0.7419 | 0.7529 | 0.08007 | 0.5819 | 0.5479 | marginal | 0.4 | 0.4 | 0.2 | 16704 | per_scenario | 3
3 | Hyperscale_LC | LowT_60C | 0.7358 | 0.7583 | 0.08007 | 0.5816 | 0.5476 | marginal | 0.4 | 0.4 | 0.2 | 16704 | per_scenario | 3
4 | Mid_LC | MidT_90C | 0.5916 | 0.7529 | 0.16285 | 0.5052 | 0.4532 | marginal | 0.4 | 0.4 | 0.2 | 35040 | per_scenario | 3
5 | Edge_LC | MidT_90C | 0.5916 | 0.7529 | 0.16285 | 0.5052 | 0.4532 | marginal | 0.4 | 0.4 | 0.2 | 35040 | per_scenario | 3
6 | Hyperscale_LC | MidT_90C | 0.586 | 0.7583 | 0.16285 | 0.5052 | 0.4531 | marginal | 0.4 | 0.4 | 0.2 | 35040 | per_scenario | 3
7 | Edge_LC | HighT_130C | 0.4556 | 0.7529 | 0.25316 | 0.4328 | 0.3681 | marginal | 0.4 | 0.4 | 0.2 | 16704 | per_scenario | 3
8 | Mid_LC | HighT_130C | 0.4556 | 0.7529 | 0.25316 | 0.4328 | 0.3681 | marginal | 0.4 | 0.4 | 0.2 | 16704 | per_scenario | 3
9 | Hyperscale_LC | HighT_130C | 0.4496 | 0.7583 | 0.25316 | 0.4325 | 0.3678 | marginal | 0.4 | 0.4 | 0.2 | 16704 | per_scenario | 3
1 | Edge_LC | LowT_60C | 0.7419 | 0.7529 | 0.05478 | 0.587 | 0.5479 | marginal | 0.4 | 0.4 | 0.2 | 16704 | per_scenario | 4
2 | Mid_LC | LowT_60C | 0.7419 | 0.7529 | 0.05478 | 0.587 | 0.5479 | marginal | 0.4 | 0.4 | 0.2 | 16704 | per_scenario | 4
3 | Hyperscale_LC | LowT_60C | 0.7358 | 0.7583 | 0.05478 | 0.5867 | 0.5476 | marginal | 0.4 | 0.4 | 0.2 | 16704 | per_scenario | 4
4 | Mid_LC | MidT_90C | 0.5916 | 0.7529 | 0.11844 | 0.5141 | 0.4532 | marginal | 0.4 | 0.4 | 0.2 | 35040 | per_scenario | 4
5 | Edge_LC | MidT_90C | 0.5916 | 0.7529 | 0.11844 | 0.5141 | 0.4532 | marginal | 0.4 | 0.4 | 0.2 | 35040 | per_scenario | 4
6 | Hyperscale_LC | MidT_90C | 0.586 | 0.7583 | 0.11844 | 0.514 | 0.4531 | marginal | 0.4 | 0.4 | 0.2 | 35040 | per_scenario | 4
7 | Edge_LC | HighT_130C | 0.4556 | 0.7529 | 0.1924 | 0.4449 | 0.3681 | marginal | 0.4 | 0.4 | 0.2 | 16704 | per_scenario | 4
8 | Mid_LC | HighT_130C | 0.4556 | 0.7529 | 0.1924 | 0.4449 | 0.3681 | marginal | 0.4 | 0.4 | 0.2 | 16704 | per_scenario | 4
9 | Hyperscale_LC | HighT_130C | 0.4496 | 0.7583 | 0.1924 | 0.4447 | 0.3678 | marginal | 0.4 | 0.4 | 0.2 | 16704 | per_scenario | 4
1 | Edge_LC | LowT_60C | 0.7419 | 0.7529 | 0.03748 | 0.5904 | 0.5479 | marginal | 0.4 | 0.4 | 0.2 | 16704 | per_scenario | 5
2 | Mid_LC | LowT_60C | 0.7419 | 0.7529 | 0.03748 | 0.5904 | 0.5479 | marginal | 0.4 | 0.4 | 0.2 | 16704 | per_scenario | 5
3 | Hyperscale_LC | LowT_60C | 0.7358 | 0.7583 | 0.03748 | 0.5901 | 0.5476 | marginal | 0.4 | 0.4 | 0.2 | 16704 | per_scenario | 5
4 | Mid_LC | MidT_90C | 0.5916 | 0.7529 | 0.08614 | 0.5206 | 0.4532 | marginal | 0.4 | 0.4 | 0.2 | 35040 | per_scenario | 5
5 | Edge_LC | MidT_90C | 0.5916 | 0.7529 | 0.08614 | 0.5206 | 0.4532 | marginal | 0.4 | 0.4 | 0.2 | 35040 | per_scenario | 5
6 | Hyperscale_LC | MidT_90C | 0.586 | 0.7583 | 0.08614 | 0.5205 | 0.4531 | marginal | 0.4 | 0.4 | 0.2 | 35040 | per_scenario | 5
7 | Edge_LC | HighT_130C | 0.4556 | 0.7529 | 0.14622 | 0.4542 | 0.3681 | marginal | 0.4 | 0.4 | 0.2 | 16704 | per_scenario | 5
8 | Mid_LC | HighT_130C | 0.4556 | 0.7529 | 0.14622 | 0.4542 | 0.3681 | marginal | 0.4 | 0.4 | 0.2 | 16704 | per_scenario | 5
9 | Hyperscale_LC | HighT_130C | 0.4496 | 0.7583 | 0.14622 | 0.4539 | 0.3678 | marginal | 0.4 | 0.4 | 0.2 | 16704 | per_scenario | 5

## DeltaTC_Convergence_LC
iteration | delta_max_is_match | delta_mean_is_match | converged | threshold | phase3_source
1 | 0.0277 | 0.02214 | FALSE | 0.01 | placeholder
2 | 0.0211 | 0.01622 | FALSE | 0.01 | placeholder
3 | 0.016 | 0.01188 | FALSE | 0.01 | placeholder
4 | 0.0122 | 0.0087 | FALSE | 0.01 | placeholder
5 | 0.0093 | 0.00639 | TRUE | 0.01 | placeholder

## Sobol_Weights_LC
metric | parameter | S1 | S1_conf | ST | ST_conf | note
Y_aggregate | beta | 0.017 | 0.0144 | 0.03 | 0.0043
Y_aggregate | gamma | 0.0884 | 0.0268 | 0.0993 | 0.0097
Y_aggregate | delta | 0.8734 | 0.0702 | 0.8905 | 0.0636
top3_stability_pct | beta | 0 | 0 | 0 | 0 | Y is constant; indices undefined (variance=0)
top3_stability_pct | gamma | 0 | 0 | 0 | 0 | Y is constant; indices undefined (variance=0)
top3_stability_pct | delta | 0 | 0 | 0 | 0 | Y is constant; indices undefined (variance=0)

## Stress_Test_LC
parameter | direction | perturbed_top3 | top3_unchanged | max_rank_shift | notes
Q_demand_peak | +20% | [Edge_LC+LowT_60C, Hyperscale_LC+LowT_60C, Mid_LC+LowT_60C] | TRUE | 0 | Score formula uses DC-side q_norm; plant Q_demand unused
Q_demand_peak | -20% | [Edge_LC+LowT_60C, Hyperscale_LC+LowT_60C, Mid_LC+LowT_60C] | TRUE | 0 | Score formula uses DC-side q_norm; plant Q_demand unused
T_required | +20% | [Edge_LC+LowT_60C, Hyperscale_LC+LowT_60C, Mid_LC+LowT_60C] | TRUE | 2
T_required | -20% | [Edge_LC+LowT_60C, Hyperscale_LC+LowT_60C, Mid_LC+LowT_60C] | TRUE | 2
distance_km | +20% | [Edge_LC+LowT_60C, Hyperscale_LC+LowT_60C, Mid_LC+LowT_60C] | TRUE | 0
distance_km | -20% | [Edge_LC+LowT_60C, Hyperscale_LC+LowT_60C, Mid_LC+LowT_60C] | TRUE | 0
delta_tc_norm | +20% | [Edge_LC+LowT_60C, Hyperscale_LC+LowT_60C, Mid_LC+LowT_60C] | TRUE | 0
delta_tc_norm | -20% | [Edge_LC+LowT_60C, Hyperscale_LC+LowT_60C, Mid_LC+LowT_60C] | TRUE | 0

## Carbon_Avoided_LC
pair | dc_name | process_name | shift_pattern | annual_hours | ri_temporal_utilization | Q_recovery_GWh_yr | CO2_avoided_tons_yr | equiv_cars_off_road | emission_factor_used
Hyperscale_LC + MidT_90C | Hyperscale_LC | MidT_90C | continuous | 8760 | 0.586 | 125.7673 | 34711.8 | 7546 | 0.276 (gas natural, EU EEA 2024)
Hyperscale_LC + LowT_60C | Hyperscale_LC | LowT_60C | 2shift | 2500 | 0.7358 | 45.0677 | 12438.7 | 2704.1 | 0.276 (gas natural, EU EEA 2024)
Hyperscale_LC + HighT_130C | Hyperscale_LC | HighT_130C | 2shift | 2500 | 0.4496 | 27.538 | 7600.5 | 1652.3 | 0.276 (gas natural, EU EEA 2024)
Mid_LC + MidT_90C | Mid_LC | MidT_90C | continuous | 8760 | 0.5916 | 16.0862 | 4439.8 | 965.2 | 0.276 (gas natural, EU EEA 2024)
Mid_LC + LowT_60C | Mid_LC | LowT_60C | 2shift | 2500 | 0.7419 | 5.7571 | 1589 | 345.4 | 0.276 (gas natural, EU EEA 2024)
Mid_LC + HighT_130C | Mid_LC | HighT_130C | 2shift | 2500 | 0.4556 | 3.5355 | 975.8 | 212.1 | 0.276 (gas natural, EU EEA 2024)
Edge_LC + MidT_90C | Edge_LC | MidT_90C | continuous | 8760 | 0.5916 | 2.4616 | 679.4 | 147.7 | 0.276 (gas natural, EU EEA 2024)
Edge_LC + LowT_60C | Edge_LC | LowT_60C | 2shift | 2500 | 0.7419 | 0.881 | 243.2 | 52.9 | 0.276 (gas natural, EU EEA 2024)
Edge_LC + HighT_130C | Edge_LC | HighT_130C | 2shift | 2500 | 0.4556 | 0.541 | 149.3 | 32.5 | 0.276 (gas natural, EU EEA 2024)

## PROMETHEE_Ranking_LC
rank_promethee | pair | phi_net | is_match_rank | rank_difference
1 | Hyperscale_LC + LowT_60C | 0.4412 | 3 | 2
2 | Hyperscale_LC + MidT_90C | 0.2366 | 6 | 4
3 | Mid_LC + LowT_60C | 0.2037 | 2 | -1
4 | Edge_LC + LowT_60C | 0.1817 | 1 | -3
5 | Mid_LC + MidT_90C | -0.0213 | 4 | -1
6 | Edge_LC + MidT_90C | -0.1042 | 5 | -1
7 | Hyperscale_LC + HighT_130C | -0.2079 | 9 | 2
8 | Mid_LC + HighT_130C | -0.3587 | 8 | 0
9 | Edge_LC + HighT_130C | -0.3711 | 7 | -2

## PROMETHEE_Correlation_LC
metric | value
spearman_rho | 0.6667
kendall_tau | 0.4444
n_pair | 9
top3_agreement | 2
weights_used_promethee | 0.25, 0.25, 0.25, 0.25
weights_used_ismatch | beta=0.40, gamma=0.40, delta=0.20
preference_function | t5 (V-shape with indifference); q=0.01, p=0.30
criteria | ri_temporal, exergy_dt_norm, one_minus_delta_tc, co2_norm

## Regulatory_KPIs
dc_scenario | plant_id | t_tier | distance_km | TWH_mean_C | T_req_C | delta_T_residual_C | ERF_scenario | Q_negotiated_mean_kW | Q_demand_plant_kW | ERF_pair | Art26_applicable | is_match_score | is_match_category | regulatory_note
Edge_LC | LowT_01_Food_Short | LowT_60C | 30 | 47.6 | 60 | 12.4 | 0.81 | 342 | 800 | 0.81 | FALSE | 0.5904 | marginal | Heat pump required (ΔT = 12°C)
Edge_LC | LowT_02_Agro_Medium | LowT_60C | 75 | 47.6 | 60 | 12.4 | 0.81 | 342 | 1200 | 0.81 | FALSE | 0.5904 | marginal | Heat pump required (ΔT = 12°C)
Edge_LC | LowT_03_Dairy_Short | LowT_60C | 45 | 47.6 | 65 | 17.4 | 0.81 | 342 | 650 | 0.81 | FALSE | 0.5904 | marginal | Heat pump required (ΔT = 17°C)
Edge_LC | MidT_04_PaperPulp_Medium | MidT_90C | 80 | 47.6 | 90 | 42.4 | 0.81 | 342 | 28127.9 | 0.81 | FALSE | 0.5206 | marginal | Heat pump required (ΔT = 42°C)
Edge_LC | MidT_05_PaperPulp_Short | MidT_90C | 50 | 47.6 | 90 | 42.4 | 0.81 | 342 | 31141.6 | 0.81 | FALSE | 0.5206 | marginal | Heat pump required (ΔT = 42°C)
Edge_LC | MidT_06_PaperPulp_Long | MidT_90C | 140 | 47.6 | 90 | 42.4 | 0.81 | 342 | 21095.9 | 0.81 | FALSE | 0.5206 | marginal | Heat pump required (ΔT = 42°C)
Edge_LC | HighT_07_Rubber_Medium | HighT_130C | 100 | 47.6 | 130 | 82.4 | 0.81 | 342 | 2800 | 0.81 | FALSE | 0.4542 | marginal | CO2-HTHP required (ΔT = 82°C)
Edge_LC | HighT_08_ChemProcess_Short | HighT_130C | 55 | 47.6 | 130 | 82.4 | 0.81 | 342 | 4500 | 0.81 | FALSE | 0.4542 | marginal | CO2-HTHP required (ΔT = 82°C)
Edge_LC | HighT_09_Steam_Long | HighT_130C | 160 | 47.6 | 135 | 87.4 | 0.81 | 342 | 6200 | 0.81 | FALSE | 0.4542 | marginal | CO2-HTHP required (ΔT = 87°C)
Mid_LC | LowT_01_Food_Short | LowT_60C | 30 | 47.6 | 60 | 12.4 | 0.81 | 2235.2 | 800 | 0.81 | TRUE | 0.5904 | marginal | Heat pump required (ΔT = 12°C)
Mid_LC | LowT_02_Agro_Medium | LowT_60C | 75 | 47.6 | 60 | 12.4 | 0.81 | 2235.2 | 1200 | 0.81 | TRUE | 0.5904 | marginal | Heat pump required (ΔT = 12°C)
Mid_LC | LowT_03_Dairy_Short | LowT_60C | 45 | 47.6 | 65 | 17.4 | 0.81 | 2235.2 | 650 | 0.81 | TRUE | 0.5904 | marginal | Heat pump required (ΔT = 17°C)
Mid_LC | MidT_04_PaperPulp_Medium | MidT_90C | 80 | 47.6 | 90 | 42.4 | 0.81 | 2235.2 | 28127.9 | 0.81 | TRUE | 0.5206 | marginal | Heat pump required (ΔT = 42°C)
Mid_LC | MidT_05_PaperPulp_Short | MidT_90C | 50 | 47.6 | 90 | 42.4 | 0.81 | 2235.2 | 31141.6 | 0.81 | TRUE | 0.5206 | marginal | Heat pump required (ΔT = 42°C)
Mid_LC | MidT_06_PaperPulp_Long | MidT_90C | 140 | 47.6 | 90 | 42.4 | 0.81 | 2235.2 | 21095.9 | 0.81 | TRUE | 0.5206 | marginal | Heat pump required (ΔT = 42°C)
Mid_LC | HighT_07_Rubber_Medium | HighT_130C | 100 | 47.6 | 130 | 82.4 | 0.81 | 2235.2 | 2800 | 0.81 | TRUE | 0.4542 | marginal | CO2-HTHP required (ΔT = 82°C)
Mid_LC | HighT_08_ChemProcess_Short | HighT_130C | 55 | 47.6 | 130 | 82.4 | 0.81 | 2235.2 | 4500 | 0.81 | TRUE | 0.4542 | marginal | CO2-HTHP required (ΔT = 82°C)
Mid_LC | HighT_09_Steam_Long | HighT_130C | 160 | 47.6 | 135 | 87.4 | 0.81 | 2235.2 | 6200 | 0.81 | TRUE | 0.4542 | marginal | CO2-HTHP required (ΔT = 87°C)
Hyperscale_LC | LowT_01_Food_Short | LowT_60C | 30 | 46 | 60 | 14 | 0.81 | 17642.6 | 800 | 0.81 | TRUE | 0.5901 | marginal | Heat pump required (ΔT = 14°C)
Hyperscale_LC | LowT_02_Agro_Medium | LowT_60C | 75 | 46 | 60 | 14 | 0.81 | 17642.6 | 1200 | 0.81 | TRUE | 0.5901 | marginal | Heat pump required (ΔT = 14°C)
Hyperscale_LC | LowT_03_Dairy_Short | LowT_60C | 45 | 46 | 65 | 19 | 0.81 | 17642.6 | 650 | 0.81 | TRUE | 0.5901 | marginal | Heat pump required (ΔT = 19°C)
Hyperscale_LC | MidT_04_PaperPulp_Medium | MidT_90C | 80 | 46 | 90 | 44 | 0.81 | 17642.6 | 28127.9 | 0.81 | TRUE | 0.5205 | marginal | Heat pump required (ΔT = 44°C)
Hyperscale_LC | MidT_05_PaperPulp_Short | MidT_90C | 50 | 46 | 90 | 44 | 0.81 | 17642.6 | 31141.6 | 0.81 | TRUE | 0.5205 | marginal | Heat pump required (ΔT = 44°C)
Hyperscale_LC | MidT_06_PaperPulp_Long | MidT_90C | 140 | 46 | 90 | 44 | 0.81 | 17642.6 | 21095.9 | 0.81 | TRUE | 0.5205 | marginal | Heat pump required (ΔT = 44°C)
Hyperscale_LC | HighT_07_Rubber_Medium | HighT_130C | 100 | 46 | 130 | 84 | 0.81 | 17642.6 | 2800 | 0.81 | TRUE | 0.4539 | marginal | CO2-HTHP required (ΔT = 84°C)
Hyperscale_LC | HighT_08_ChemProcess_Short | HighT_130C | 55 | 46 | 130 | 84 | 0.81 | 17642.6 | 4500 | 0.81 | TRUE | 0.4539 | marginal | CO2-HTHP required (ΔT = 84°C)
Hyperscale_LC | HighT_09_Steam_Long | HighT_130C | 160 | 46 | 135 | 89 | 0.81 | 17642.6 | 6200 | 0.81 | TRUE | 0.4539 | marginal | CO2-HTHP required (ΔT = 89°C)